## Slide 1: Optimal Power Flow: Closing the Loop over Corrupted Data
André Teixeira, Henrik Sandberg, György Dán, and Karl H. Johansson
ACCESS Linnaeus Centre, KTH Royal Institute of Technology
American Control Conference
Montréal, June 28th, 2012

## Slide 2: Motivation
Networked control systems are becoming more pervasive
  Increasing use of ”open” networks and COTS
Infrastructures are becoming more vulnerable to cyber-threats!
  Several attack points
Nature-driven events are known to have caused severe disruptions
A major concern is the possible impact of cyber threats on these systems

## Slide 3: Power Transmission Networks
Previous work
  Vulnerabilities of current SCADA/EMS systems to data attacks on measurements
Current work
  Consequences on system operation: Optimal Power Flow
SCADA: Supervisory Control and Data Acquisition

## Slide 4: Cyber Security of State Estimator in Power Networks
State Estimator: estimates the state and unmeasured variables
Bad Data Detector: detects and removes corrupted measurements
Can data attacks affect the SE without being detected?
  Yes! [Liu et al, 2009]

## Slide 5: DC Network Model
Only active power:
  Similar to a DC resistive network
Simplifications:
  No resistances or shunt elements
Measurement model:
Linear Least Squares Estimator:
Measurement residual:
Bad Data Detector:

## Slide 6: Attacker Model
Corrupted measurements:
Attacker’s objectives:
  Attack is stealthy (undetectable)
  Target measurements are corrupted
Least-effort attacks are more likely
Larger effort increased security
  : set of stealthy attacks
  : set of goals
  : set of constraints
and are scenario specific
Minimum effort attacks:

## Slide 7: Security Metric for Stealthy Attacks
is the security metric for the k-th measurement
  is the optimal solution of
Minimum number of attacked measurements so that
  Attack is stealthy
  Measurement is corrupted
[Sandberg et al, 2010]
[Sou et al, 2011]

## Slide 8: Cyber Security of Optimal Power Flow in Power Networks
How do stealthy attacks affect the power system’s operation?
  Related work: [Xie et al, 2010], [Yuan et al, 2011]
Optimal Power Flow
  Computes generator setpoints minimizing operation costs
  Ensures operation constraints

## Slide 9: DC-Optimal Power Flow
Optimal power generation
  However may not be measured
DC-Optimal Power Flow considers the lossless DC model
  power demand
  power generation
Operation costs:
  Generation costs
  Transmission losses
$
$
$
$

## Slide 10: DC-Optimal Power Flow Nominal Operation
At optimality, the KKT conditions hold:
Lagrangian function:

## Slide 11: DC-Optimal Power Flow under attack
The estimate is given by the State Estimator
  vulnerable to cyber attacks
Suppose the system is in optimality with and
Operation under Data Attacks
Ficticious operating conditions
Proposed control action
When would an operator apply the proposed control action?
What would be the resulting operating cost?

## Slide 12: DC-Optimal Power Flow under attack
Assume the attack does not change the active constraints
  thus are known
The proposed control action is given by
  is an affine map w.r.t

## Slide 13: Estimated Re-Dispatch Profit
Consider the corrupted estimates and
  : estimated operation cost
  : estimated optimal operation cost given
  : estimated re-dispatch profit
Large estimated profit may lead the operator to apply
Ficticious operating conditions
Proposed control action

## Slide 14: True Re-Dispatch Profit
Mismatches between and are compensated by slack generators
  can be modeled as an affine map w.r.t :
  : true operation cost after re-dispatch
  : true re-dispatch profit
Large means more ”dangerous” attacks (larger impact)
Proposed control action
True generation profile
Slack
generators

## Slide 15: VIKING Benchmark: Impact of Data Attacks
Cost function corresponds to the total resistive losses
Sparse attacks are computed from the previous security metric
is computed for each sparse attack

## Slide 16: VIKING Benchmark: Impact of Data Attacks
Security metric
  Are all the sparse attacks equally dangerous?
Impact of Data Attacks
  Most sparse attacks have low impact on operation cost
Target measurement index
Target measurement index

## Slide 17: Impact-Aware Security Metric
is the impact-aware security metric for the k-th measurement
  is the optimal solution of
Similar to the previous security metric
  Sensitive to the choice of parameters

## Slide 18: Summary
  The effects of data attacks on the DC-OPF were analyzed and analytically characterized
  The estimated and true profit were introduced
  A novel impact-aware security metric was proposed
Thank you
Questions?

## Slide 19: Impact-Aware Security Metric
is the impact-aware security metric for the k-th measurement (cf. )
  is the optimal solution of
Maximum impact to the network operation cost so that
  Attacks are stealthy with a given sparsity
  Measurement is corrupted